CONFIGURED DRIVE SYSTEM STORAGE INSTRUCTIONS

If it is necessary to store the drive system for any length of time prior to installation, it must be stored according to the following instructions:

- The drive system should remain in its shipping container during storage.

- Wrap the drive system in a covering of heavy-duty plastic or similar material to prevent the entry of dirt and dust.

- Drive systems not installed and energized immediately should be stored in a clean, dry place.  Allowable storage temperature range is -25o to 55 o C (-13 o to 130 o F).

- It is preferable to store the drive system in a heated building that offers stable temperatures and adequate air circulation and protection from dirt and water. If the storage temperature fluctuates, or humidity exceeds 60%, it will be necessary to use space heaters to prevent condensation.  Rockwell makes no recommendation as to space heater ratings and cautions those responsible for safe storage of drives to remove all combustible material and properly set up any temporary heaters safely, so as not to overheat an enclosure or cause a fire.

- Drive systems that are designed for indoor applications do not have sufficient packaging protection for outdoor storage. Outdoor storage is not recommended for indoor rated enclosures.

- Do not store equipment where it is exposed to a corrosive atmosphere i.e. salt spray, Chlorine gas or Hydrogen Sulfide, etc.

- Do not store equipment in a construction area or other locations where it might be subjected to falling or flying debris, improper handling or other construction hazards.